## Titles
TITLE BLOCK
Company | XLNControl Pty Ltd
Document No | XLN-DRW-INST-0231
Project | Plant Upgrade Project
Project No | PRJ-EXP-2020
Additional Info | Utlitities Area Expansion
Revision Information
Revision | Date | Revision Comment | Drawn | Checked | Approved
1 | 2020-02-15 | Issued for comment | NM | MN | XLNC
2 | 2020-04-25 | Issued for construction | NM | MN | XLNC
Logo file Path
C:\Pictures\logo.png
DRAWING HEADER
This location information is shown on the top of all the loop drawings
Location 1 | FIELD
Location 2 | REMOTE I/O

## Data
Loop |  | Instrument | [11 empty] | Junction Box | [6 empty] | Marshalling Rack |  |  |  | Barrier / Relay |  |  |  |  | ext power from relay |  | Field termination assembly |  |  |  |  | Control System
Loop Name | Service | Tag Name | Description | Additional field1 | Additional field2 | Shielded? | Terminal 1 | Terminal 2 | Ground Terminal | Wire color1 | Wire color2 | Instrument Cable | Additional field | Name | Terminal 1 | Terminal 2 | Ground Terminal | Cable Name | Pair no | Additional field | Name | Terminal 1 | Terminal 2 | Ground Terminal | Name | Left Terminal 1 | Left Terminal 2 | Right Terminal 1 | Right Terminal 2 | Location | Supply | Name | Terminal 1 | Terminal 2 | System Cable | Additional field | Controller | Tag | Rack | Slot | Channel
T-23432 | Temp Control (2 wire loops) | TT-23432 | Reboiler temperature | 0 to 200 °C | Make: XLNC | Yes | 1 | 2 | 3 | BLK | WHT | TT32 | 3 sq mm | JB-234 | 45 | 46 | 47 | J-234 | 3 | 24 core | MR-234 | 1+ | 1- | G | [7 empty] | FTA-23 | 4 | 5 | SYS-4 | Type 1 | PLC-1 | TI23432 | 2 | 5 | 4
T-23432 | Temp Control (2 wire loops) | TV-23432 | Temp Control Valve | 0 to 100 % | Model: XLNC | No | 1 | 2 |  | BLK | WHT | TV32 | 3 sq mm | JB-234 | 50 | 51 |  | J-234 | 2 | 24 core | MR-234 | 5+ | 5- | [8 empty] | FTA-31 | 1 | 2 | SYS-7 | Type 2 | PLC-1 | TV23432 | 3 | 5 | 2
A-54761 | Process Analyser (4 wire loop) | AI-54761 | Dew Point Analyser | 0 to 50 °C | Make: APS | Yes | 1+ | 1- | G | BLK | WHT | AT12 | 3 sq mm | JB-235 | 13 | 14 | 15 | J-235 | 1 | 12 core | MR-235 | 3+ | 3- | G | [7 empty] | FTA-22 | 5 | 3 | SYS-4 | Type 1 | PLC-1 | AI54761 | 1 | 5 | 3
A-54761 | Process Analyser (4 wire loop) | AP-54761 | 230 V AC Power |  |  | Yes | 3 | 4 | 5 | RED | BRN | AP23 | 4 sq mm | [7 empty] | SS12 / Q24 | L | N | E
F-32654 | Flow meter (4 wire loop) | FI-32654 | Mass flow meter | 0 to 100 kg/h | Model: XLNC | No | 1 | 2 |  | BLK | WHT | F11 | 3 sq mm | JB-234 | 25 | 26 |  | J-237 | 10 | 12 core | MR-237 | 8 | 9 |  | BR1 | A | B | C | D |  |  | FTA-23 | 5 | 6 | SYS-4 | Type 1 | PLC-1 | FI32654 | 1 | 2 | 4
F-32654 | Flow meter (4 wire loop) | FP-32654 | 24 V DC Supply |  |  | No | P | N |  | RED | BLK | P11 | 4 sq mm | [7 empty] | MR-237 | 10 | 11
P-33432 | Vessel Pressure (Straight run cable) | PT-33432 | Vessel Pressure | 0 to 200 psi | Make: XLNC | Yes | 1 | 2 | 3 | BLK | WHT | PT32 | 3 sq mm | [7 empty] | MR-304 | 2 | 3 | 4 | [7 empty] | FTA-23 | 7 | 8 | SYS-4 | Type 1 | PLC-2 | PI33432 | 4 | 1 | 4
T-73432 | Reactor Temperature (Loop with IS Barrier) | TT-73432 | Reactor temperature | 0 to 350 °C | Model: XLNC | Yes | 1 | 2 | 3 | BLK | WHT | F11 | 4 sq mm | JB-234 | 25 | 26 | 27 | J-234 | 5 | 12 core | MR-238 | 8 | 9 | 10 | BR1 | A | B | C | D |  |  | FTA-32 | 5 | 6 | SYS-4 | Type 1 | PLC-3 | TT73432 | 2 | 2 | 4
S-73454 | Siren (Loops with relay) | SN-73454 | Converyor Siren 1 | Warning siren | Model: XLNC | Yes | 1 | 2 | 3 | RED | BLK | F12 | 4 sq mm | JB-235 | 25 | 26 | 27 | J-235 | 3 | 12 core | MR-338 | 8 | 9 | 10 | RL1 | 1 | 2 | 3 | 4 | Bottom Wire | - 24 V + | FTA-30 | 5 | 6 | SYS-5 | Type 3 | PLC-4 | SN73454 | 3 | 2 | 2
S-73454 | Siren (Loops with relay) | SN-73455 | Converyor Siren 2 | Warning siren | Model: XLNC | Yes | 1 | 2 | 3 | RED | BLK | F13 | 4 sq mm | JB-236 | 25 | 26 | 27 | J-236 | 4 | 12 core | MR-338 | 3 | 4 | 5 | RL2 | 1 | 2 | 3 | 4 | Top Wire | + 24 V - | FTA-30 | 7 | 8 | SYS-5 | Type 3 | PLC-4 | SN73455 | 3 | 2 | 4